THERMAL INSULATION

SECTION 07 21 19

Foamed-in-Place Insulation

Classic Ultra Select

This specification utilizes the Construction Specifications Institute’s (CSI) 3-Part formatting.  The specification is a manufacturer-specific product specification to be used by design professionals as a guide specification.  Editing notes are indicated in red italics and precede specification text.  Delete editing notes in final specification.

This specification specifies medium density spray foam insulation by Huntsman Building Solutions.  Revise section number and title below to suit project requirements.

The specified product may contribute to the following credits/points for the respective rating system:

LEED V.4.1

National Green Building Standard (NGBS, ICC-700)

ERI (Energy Rating Index)

.

- GENERAL

  - SECTION INCLUDES

** NOTE TO SPECIFIER **  Delete items below not required for project.

    - Spray-in-place semi-rigid open cell ½ pound polyurethane foam insulation in various assemblies, to provide an air barrier and improved thermal resistance.

  - RELATED SECTIONS

** NOTE TO SPECIFIER **  Delete any sections below not relevant to this project; add others as required.

    - Section 03 30 00 - Cast in Place Concrete.

    - Section 03 40 00 - Structural Pre-cast Concrete.

    - Section 04 20 00 - Unit Masonry.

    - Section 05 30 00 - Metal Decking.

    - Section 05 40 00 - Cold Formed Metal Framing.

    - Section 06 10 00 - Rough Carpentry.

    - Section 07 10 00 - Waterproofing.

    - Section 07 26 00 - Vapor Barrier.

    - Section 07 40 00 - Preformed Roofing and Cladding/Siding.

    - Section 07 65 00 - Flexible Flashing.

    - Section 07 80 00 – Fire protection.

    - Section 07 81 00 – Applied Fireproofing.

    - Section 09 20 00 - Gypsum Board.

    - Section 09 22 00 - Metal Support Systems.

  - REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not actually required by the text of the edited section.

    - American Society for Testing and Materials (ASTM):

      - ASTM D 1622 Standard Test Method for Apparent Density of Rigid Cellular Plastics

      - ASTM C 518 Standard Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus

      - ASTM E 2178 Standard Test Method for Determining Air Leakage Rate and Calculation of Air Permeance of Building Materials

      - ASTM E 96 Standard Test Methods for Water Vapor Transmission of Materials

      - ASTM D 2842 Standard Test Method for Water Absorption of Rigid Cellular Plastics

      - ASTM D 2126 Standard Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging

      - ASTM E 84 Standard Test Method for Surface Burning Characteristics of Building Materials

      - ASTM E 119 Standard Test Methods for Fire Tests of Building Construction and Materials

      - ASTM E 970 Standard Test Method for Critical Radiant Flux of Exposed Attic Floor Insulation Using a Radiant Heat Energy Source

    - National Fire Protection Association (NFPA):

      - NFPA 286 Standard Methods of Fire Tests for Evaluating Contribution of Wall and Ceiling Interior Finish to Room Fire Growth

      - NFPA 285 Standard Fire Test Method for Evaluation of Fire Propagation Characteristics of Exterior Wall Assemblies Containing Combustible Components

    - International Code Council – International Residential Code:

      - Section 103.7 - Alternate Materials and Methods.

      - 2012, 2015, 2018, 2021 IRC Section R314 - Foam Plastic Insulation.

      - 2012, 2015, 2018, 2021 IRC Section R316 - Foam Plastic Insulation.

      - IRC Section R806.5 Unvented Attic and Unvented Enclosed Rafter Assemblies.

    - International Code Council – International Building Code:

      - Section 104.11 Alternative materials, design and methods of construction and equipment.

      - Section 2603 Foam Plastic Insulation.

      - Section 1203.3 – Unvented Attic and Unvented Enclosed Rafter Assemblies.

(IBC Versions 2012, 2015, 2018, 2021)

  - SUBMITTALS

    - Submit under provisions of Section 01300.

    - Before commencing work, submit in accordance with local code.

      - Submit technical data sheets and samples as required by local code officials.

      - Submit the technical data sheet from the manufacturer showing the test results from the ASTM E84 (Surface Burning Characteristics).

      - Submit End Use Configuration Testing Compliance (ESR 1826 Section 4.4.1.2.2)

    - Product Data: Manufacturer's data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation methods.

  - QUALITY ASSURANCE

    - Installer Qualifications:

      - Contractor performing work under this section shall be authorized by HUNTSMAN BUILDING SOLUTIONS in the art of applying spray polyurethane foam insulation.

      - Provide current HUNTSMAN BUILDING SOLUTIONS Authorized Contractor Certificate.

** NOTE TO SPECIFIER ** Include a mock-up if the project size and/or quality warrant taking such a precaution.  The following is one example of how a mock-up on a large project might be specified.  When deciding on the extent of the mock-up, consider all the major different types of work on the project.

    - Mock-Up:  Provide a mock-up for evaluation of surface preparation techniques and application workmanship.

      - Finish areas designated by Architect.

      - Do not proceed with remaining work until installation is approved by Architect.

      - Rework mock-up area as required to produce acceptable work.

  - DELIVERY, STORAGE, AND HANDLING

    - Materials shall be delivered in manufacturer’s original containers clearly labelled with manufacturer’s name, product identification, safety information, net weight of contents and expiration date.

    - Material shall be stored in a safe manner and where the temperatures are in the limits specified by the material manufacturer.

    - Empty containers shall be removed from site on a daily basis.

    - Store and dispose of solvent-based materials, and materials used with solvent-based materials, in accordance with requirements of local authorities having jurisdiction.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results.  Do not install products under environmental conditions outside manufacturer's absolute limits.

    - Ventilate insulation application area in accordance with the Spray Foam Coalition’s Guidance on best practices for the installation of Spray Polyurethane Foam.

    - Protect workers as recommended by the Spray Foam Coalition’s Guidance on best practices for the installation of Spray Polyurethane Foam.

    - Protect adjacent surfaces, windows, equipment and site areas from damage of overspray.

  - WARRANTY

    - Manufacturer’s Warranty:  HUNTSMAN BUILDING SOLUTIONS warrants spray-in-place urethane foam insulation, when installed by certified contractors using factory-trained applicators and applied in accordance with the Installation Instructions, will perform as stated in the Product Technical Data Sheet.

      - This warranty is in effect throughout the life of the building provided the original purchaser registers with the Warranty Department of the Manufacturer within thirty days of occupancy.

      - Manufacturer’s sole responsibility under this Limited Lifetime Warranty shall be to repair or replace any defective Product at the cost of the material only.

      - Manufacturer shall not be responsible for labor cost or any other costs whatsoever related to, or in connection with the removal or installation of either the original or replacement product.

      - Refer to www.huntsmanbuildingsolutions.com for full warranty terms.

- PRODUCTS

  - ENVIRONNEMENTAL REQUIREMENTS

    - The product shall have a generic industry Environmental Product Declaration (EPD).

  - MANUFACTURERS

    - Acceptable Manufacturer:  HUNTSMAN BUILDING SOLUTIONS

- 3315 East Division Street, Arlington, TX 76011.

- (855) 942-7273.

- architect@huntsmanbuilds.com

- http://www.huntsmanbuildingsolutions.com

** NOTE TO SPECIFIER ** Delete two of the following three paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions: Equivalent as judged by Architect

      - Contact HUNTSMAN BUILDING SOLUTIONS Building Science and Engineering Department for product comparison data

        - 855-942-7273

        - architect@huntsmanbuilds.com

  - SPRAY FOAM INSULATION

** NOTE TO SPECIFIER **. Delete if not required.

    - Spray Applied Semi Rigid Polyurethane Foam Insulation System: Open Cell ½ pound Foam Product: Classic Ultra Select

      - Manufactured by HUNTSMAN BUILDING SOLUTIONS, Arlington, TX.

      - Product Approval:

        - International Code Council Evaluation Services Report #1826

- Approved for building types I, II, III, IV, & V

        - Passed NFPA 286

      - Installation:

        - Application with a prescriptive Thermal Barrier:

          - There is no thickness limit when installed behind a code -prescribed 15-minute thermal barrier, (.5 inch Gypsum Wall Board), per ICC ESR 1826 Section 4.3.1.1.

        - Application without a prescriptive Thermal Barrier:

          - With DC 315 Intumescent Coating: Up to 8.5 inches (216 mm) thick in walls and vertical surfaces, 14 inches (356 mm) thick on ceilings, underside of roof sheathing/rafters and floors with all foam surfaces covered with 14 wet mils (0.364 mm)

          - With Fireshell F10E Intumescent Coating: Up to Up to 7.5 inches (191 mm) thick in walls and vertical surfaces, 11.5 inches (292 mm) thick on ceilings, underside of roof sheathing/rafters and floors with all foam surfaces covered with 21 wet mils (0.546 mm)

        - Use in Attics: Application without a prescriptive Ignition Barrier:

- (Entry to the attic is only for service of utilities and no 					storage is permitted.)

The thickness of the foam plastic applied to the underside of 										 the roof sheathing must not exceed 14 inches (356 mm). 											 The thickness of the spray foam insulation applied to vertical 									    	 wall surfaces must not exceed 5.5 inches (140 mm).

          - With DC 315 Intumescent Coating: All foam surfaces must be covered with 4 wet mils (0.1mm)

          - With NO Burn Plus XD Intumescent Coating: All foam surfaces must be covered with 6 wet mils (0.15mm)

        - Use in Unvented Attics and Unvented Enclosed Rafter Assemblies in accordance with IRC R806.5 and IBC 1203.3.

- Application without an Ignition Barrier or Intumescent coating 	(Exposed foam)

- (Entry to the attic is only for service of utilities and no storage is 	permitted.)

The insulation may be applied to the underside of roof sheathing 									and/or rafters to a minimum thickness 3.5 inches (89 mm) and 										may be  applied to vertical wall surfaces to a minimum of 3.5 										inches (89 mm). Maximum thickness on the underside of roof 										sheathing or on vertical wall surfaces is 20 inches (508 mm). The 									insulation may	be left exposed to the attic without a prescriptive 									ignition barrier or an intumescent coating.

The attic must have attic access complying with IRC section 										R807, horizontally placed in the floor, and opening downward 										toward the living space.

        - Use on Attic Floors:

Up to 11.5 inches (292 mm) between and over the joists in an attic 								floor.  No ignition barrier or intumescent coating is required over  									the foam.

        - One-Hour Fire-Resistance-Rated Wall Assemblies:

          - Refer to ESR 1826 Section 4.5

      - Physical Properties:

| - Density | ASTM D1622 | 0.5 lb/ft³ | 8 Kg/m³ |
| --- | --- | --- | --- |
| Thermal Resistance | ASTMC518 at 1’’ | R- 3.7 | 0.65 RSI |
| Dimensional Stability | ASTM D-2126 (% of change in volume at 28 days) 158°F (70°C) 97% R.H. | 0.0 % |  |
| Surface burning characteristics | ASTM E84 | Class 1 |  |
| Flame spread index | ASTM E84 | 20 |  |
| Smoke development | ASTM E84 | 340 |  |
| Air Permeance | ASTM E 2178 at 3’’ | <0.014 L/s· m² |  |
| Water Absorption | ASTM D 2842 | 5% |  |
| Water vapor permeance | ASTM E96 (5.5’’) | 11 perms | 629 ng/Pa s.m² |
| Ignition Properties | ASTM D1929 | 968oF | 520oC |
| Commercial Fire Resistance | ASTM E 119 | 1,2 & 3 hours Ratings |  |
| Commercial Fire Resistance | NFPA 285 | Assembly Passed |  |
| Attic Floor Uncoated Thickness | ASTM 970 | 11.5’’ |  |
| Limited Access Crawl Space Walls & Roof uncoated Thickness | End Use Configuration | Walls: 3.5’’ – Roof: 14’’ |  |
| Limited Access Attic Walls & Roof Uncoated Thickness | End Use Configuration | Walls: 20’’ – Roof: 20’’ |  |
| Walls and Ceiling Application Maximum Thickness / Behind Prescriptive Thermal Barrier | NFPA 286 | Walls: No Limit – Ceiling: No Limit |  |
| Sound Transmission Class | ASTM E 90 | 125 Hertz: STC 19 250 Hertz: STC 30 500 Hertz: STC 31 1000 Hertz: STC 42 2000 Hertz: STC 38 4000 Hertz: STC 46 |  |
| Noise reduction Coefficient | ASTM C 423 | 125 Hertz: NRC .11 250 Hertz: NRC .43 500 Hertz: NRC .89 1000 Hertz: NRC .72 2000 Hertz: NRC .71 4000 Hertz: NRC .67 |  |

      - Equipment used to apply the foam insulation shall have fixed ratio positive displacement pumps and approved by foam manufacturer.

      - Equipment used to apply the Water Based intumescing coating shall be an airless sprayer    approved by the manufacturer.

  - ACCESSORY PRODUCTS

- A.       Water Based intumescing coatings:

      - Product: DC 315, Manufactured by International Fireproof Technology, Inc.

- ESR 3702

      - Product: Fireshell F10E, Manufactured by ICP Building Solutions Group

ESR 3997

      - Product: No-Burn® Plus XD, Manufactured by No-Burn Inc.

ESR 3102

    - Primers:

      - Product: Adbond manufactured by Adfast or Thermo-Prime by HUNTSMAN

- BUILDING SOLUTIONS

        - Application: Follow manufacturer’s application recommendations.

        - Recommended for oily surfaces and galvanized steel like Z-bar, PVC, curtain walls and steel decks

- EXECUTION

  - EXAMINATION

    - Do not begin installation until substrates have been properly prepared.

    - If substrate preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

    - Commencement of work outlined in this section shall be deemed as acceptance of existing work and conditions.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Apply only when surfaces and environmental conditions are within limits prescribed by the material manufacturer.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

    - It is recommended to install primer on oily surfaces and galvanized steel

  - INSTALLATION

    - Install in accordance with manufacturer's instructions.

    - Apply as recommended by manufacturer to thickness as indicated on drawings.

    - Equipment used to apply the foam insulation shall have fixed ratio positive

- displacement pumps approved by foam manufacturer.

  - PROTECTION

    - Protect installed products until completion of project.

    - Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION 07 21 19