THERMAL INSULATION

SECTION 07 21 19

Foamed-in-Place Insulation

ProSeal LETM

This specification utilizes the Construction Specifications Institute’s (CSI) 3-Part formatting.  The specification is a manufacturer-specific product specification to be used by design professionals as a guide specification.  Editing notes are indicated in red italics and precede specification text.  Delete editing notes in final specification.  Metric conversion, where used, is soft metric conversion.

This specification specifies medium density spray foam insulation by HUNTSMAN BUILDING SOLUTIONS.  Revise section number and title below to suit project requirements.

The specified product may contribute to the following credits/points for the respective rating system:

LEED V.4.1

National Green Building Standard (NGBS, ICC-700)

ERI (Energy Rating Index)

GENERAL

SECTION INCLUDES

** NOTE TO SPECIFIER ** Delete items below not required for project.

Spray-in-place rigid closed cell 2-pound polyurethane foam insulation in various

assemblies, to provide an air barrier and improved thermal resistance.

RELATED SECTIONS

** NOTE TO SPECIFIER ** Delete any sections below not relevant to this project; add others as required.

    - Section 03 30 00 - Cast in Place Concrete.

Section 03 40 00 - Structural Pre-cast Concrete.

Section 04 20 00 - Unit Masonry.

Section 05 30 00 - Metal Decking.

Section 05 40 00 - Cold Formed Metal Framing.

Section 06 10 00 - Rough Carpentry.

Section 07 10 00 - Waterproofing.

Section 07 26 00 - Vapor Barrier.

Section 07 40 00 - Preformed Roofing and Cladding/Siding.

Section 07 65 00 - Flexible Flashing.

Section 07 80 00 – Fire protection.

Section 07 81 00 - Applied Fireproofing.

Section 09 20 00 - Gypsum Board.

Section 09 22 00 - Metal Support Systems.

REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not actually required by the text of the edited section.

    - American Society for Testing and Materials (ASTM):

      - ASTM C 518 Standard Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus

ASTM D 1621 Standard Test Method for Compressive Properties of Rigid Cellular Plastics

ASTM D 1622 Standard Test Method for Apparent Density of Rigid Cellular Plastics

ASTM D 2126 Standard Test Method for Response of Rigid Cellular Plastics to Thermal and Humid Aging

ASTM D 2842 Standard Test Method for Water Absorption of Rigid Cellular Plastics

ASTM D6226 Standard Test Method for Open Cell Content of Rigid Cellular Plastics

ASTM E 84 Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM E 96 Standard Test Methods for Water Vapor Transmission of Materials

ASTM E 119 Standard Test Methods for Fire Tests of Building Construction and Materials

ASTM E 2178 Standard Test Method for Determining Air Leakage Rate and Calculation of Air Permeance of Building Materials

National Fire Protection Association (NFPA):

NFPA 285 Standard Fire Test Method for Evaluation of Fire Propagation Characteristics of Exterior Wall Assemblies Containing Combustible Components

NFPA 286 Standard Methods of Fire Tests for Evaluating Contribution of Wall and Ceiling Interior Finish to Room Fire Growth

International Code Council

AC377 Acceptance Criteria for Spray-Applied Foam Plastic Insulation

International Code Council – International Residential Code:

Section R104.11 - Alternate materials, design and methods of construction and equipment.

Section R316 - Foam Plastic Insulation.

Section R806.5 Unvented attic and unvented enclosed rafter assemblies.

International Code Council – International Building Code:

Section 104.11 Alternative materials, design, and methods of construction and

equipment.

Section 1203.3 Unvented attic and unvented enclosed rafter assemblies.

Section 2603 Foam Plastic Insulation.

SUBMITTALS

    - Submit under provisions of Section 01 30 00.

Before commencing work, submit in accordance with local code.

Submit technical data sheets and samples as required by local code officials.

Submit the technical data sheet from the manufacturer showing the test results

from the ASTM E84 (Surface Burning Characteristics).

Submit AC377 Appendix X compliance.

Product Data: Manufacturer's data sheets on each product to be used,	including:

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Installation methods.

QUALITY ASSURANCE

    - Installer Qualifications:

Contractor performing work under this section shall be authorized by

Huntsman Building Solutions in the art of applying spray polyurethane foam insulation.

Provide current HUNTSMAN BUILDING SOLUTIONS Authorized Contractor

Certificate.

** NOTE TO SPECIFIER ** Include a mock-up if the project size and/or quality warrant taking such a precaution.  The following is one example of how a mock-up on a large project might be specified.  When deciding on the extent of the mock-up, consider all the major different types of work on the project.

Mock-Up:  Provide a mock-up for evaluation of surface preparation techniques and

application workmanship.

Finish areas designated by Architect.

Do not proceed with remaining work until installation is approved by Architect.

Rework mock-up area as required to produce acceptable work.

DELIVERY, STORAGE, AND HANDLING

    - Materials shall be delivered in manufacturer’s original containers clearly labelled

with manufacturer’s name, product identification, safety information, net weight of

contents and expiration date.

Material shall be stored in a safe manner and where the temperatures are in the

limits specified by the material manufacturer.

Empty containers shall be removed from site daily.

Store and dispose of solvent-based materials, and materials used with solvent-

based materials, in accordance with requirements of local authorities having

jurisdiction.

PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within

limits recommended by manufacturer for optimum results.  Do not install products

under environmental conditions outside manufacturer's absolute limits.

Ventilate insulation application area in accordance with the Spray Foam Coalition’s

Guidance on best practices for the installation of Spray Polyurethane Foam.

Protect workers as recommended by the Spray Foam Coalition’s Guidance on best

practices for the installation of Spray Polyurethane Foam.

Protect adjacent surfaces, windows, equipment, and site areas from damage	of overspray.

WARRANTY

    - Manufacturer’s Warranty:  HUNTSMAN BUILDING SOLUTIONS warrants spray-in-

place urethane foam insulation, when installed by certified contractors using factory-

trained applicators and applied in accordance with the Installation Instructions, will

perform as stated in the Product Technical Data Sheet.

This warranty is in effect throughout the life of the building provided the original purchaser registers with the Warranty Department of the Manufacturer within thirty days of occupancy.

Manufacturer’s sole responsibility under this Limited Lifetime Warranty shall be to repair or replace any defective Product at the cost of the material only.

Manufacturer shall not be responsible for labor cost or any other costs whatsoever related to, or in connection with the removal or installation of either the original or replacement product.

Refer to www.huntsmanbuildingsolutions.com for full warranty terms.

PRODUCTS

MANUFACTURERS

    - Acceptable Manufacturer:  HUNTSMAN BUILDING SOLUTIONS

3315 East Division Street, Arlington, TX 76011.

(855) 942-7273

architect@huntsmanbuilds.com

http://www.huntsmanbuildingsolutions.com

** NOTE TO SPECIFIER ** Delete two of the following three paragraphs: coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions: Equivalent as judged by Architect

      - Contact HUNTSMAN BUILDING SOLUTIONS Building Science and Engineering Department for product comparison data

        - (855) 942-7273

        - architect@huntsmanbuilds.com

Requests for substitutions will be considered in accordance with provisions of Section 01600.

SPRAY FOAM INSULATION

    - Spray Applied Rigid Polyurethane Foam Insulation System: ProSeal LE

Manufacturer: HUNTSMAN BUILDING SOLUTIONS, Arlington, TX

Product Approval:

ICC-ES Evaluation Report ESR-3500

Approved for use in building types I, II, III, IV, and V construction under IBC and dwellings for IRC.

AC377 Appendix X compliant NFPA 286.

Application Options:

Application with a prescriptive Thermal Barrier:

There is no thickness limit when installed in floors or ceilings behind 1/2-inch gypsum wall board or equivalent 15-minute thermal barrier in accordance with IBC 2603.4 or IRC R316.4.

Application without a prescriptive Thermal Barrier:

Up to 9 -1/2 inches (241 mm) thickness on the underside of the roof sheathing/rafters and floors and 5-1/2 inches (140 mm) in wall cavities and attic floors with:

A minimum of 14 wet mils of DC-315 Intumescent Paint

Up to 11 -1/4 inches (286 mm) thickness on the underside of the roof sheathing/rafters and floors and 7-1/2 inches (191 mm) in wall cavities and attic floors with:

A minimum of 18 wet mils of Fireshell F10E intumescent Paint

Up to 8 inches (203 mm) thickness on the underside of the roof sheathing/rafters and floors and 4 inches (102 mm) in wall cavities and attic floors with:

(a)     A minimum of 14 wet mils of No-Burn Plus ThB Intumescent Paint

Attics and Crawlspaces: Application without a prescriptive ignition barrier (Entry to the attic or crawlspace is only to service utilities and No storage is permitted.) Minimum application thickness of 1 inch.

Attics and Crawlspaces: Application without a prescriptive ignition barrier or intumescent coating

Passed AC377 Appendix X compliant NFPA 286. (Entry to the attic or crawlspace is only to service utilities and No storage is permitted.)

Maximum thickness on walls is 6 inches (152 mm), maximum thickness on underside of roofs and wood floors is 8 inches (203 mm).

Use on Attic Floors:

Up to 8 inches (203 mm) between and over the joists in attic floors

Use as a Class II vapor retarder @ < 1.0 perm, ProSeal LE minimum thickness of 1.5 inches (38 mm).

Physical Properties:

| Density | ASTM D1622 | 2.2 lb/ft³ | 32 Kg/m³ |
| --- | --- | --- | --- |
| Thermal Resistance | ASTM C518 | 1’’ = R- 7.1 2’’ = R-14 3’’ = R-21 3.5’’ = R-24 | 25.4 mm = 1.3 RSI 50.5 mm = 2.47 RSI 76.2 mm = 3.69 RSI 88.9 mm = 4.23 RSI |
| Dimensional Stability | ASTM D-2126 (% of change in volume at 7 days) 158°F, 97% R.H. | 8.9% |
| Surface burning characteristics | ASTM E84 | Class A |
| Flame spread index | ASTM E84 | 25 |
| Smoke development | ASTM E84 | 300 |
| Air Permeance | ASTM E 2178 at 1’’ | <0.02 L/s· m² |
| Water vapor permeance | ASTM E96 (1.5’’) Class II Vapor Retarder | 0.97 perms | 55.51 ng/Pa s.m² |
| Compressive Strength | ASTM D 1621 | 40 psi | 276 kPa |
| Closed Cell Content | ASTM D 6226 | 98% |
| Commercial Fire Resistance | ASTM E 119 | 1, 2 & 3 hours rating |
| Commercial Fire Resistance | NFPA 285 | Assembly Passed |
| Attic & Crawl Space Walls & Roof Uncoated Thickness | AC377 Appendix X | Walls: 6’’ – Roof: 8’’ |
| Walls and Ceiling Application Maximum Thickness | AC377 | No limit |

ACCESSORY PRODUCTS

    - Water Based Intumescing coatings:

Product: DC315, Manufactured by International Fireproof Technology, Inc.

Product: Fireshell F10E, Manufactured by ICP Building Solutions Group

Product: No-Burn Plus ThB, Manufactured by No-Burn, Inc.

Primers:

Product: Adbond manufactured by Adfast or Thermo-Prime by HUNTSMAN

BUILDING SOLUTIONS

Application: Follow manufacturer’s application recommendations.

Recommended for oily surfaces and galvanized steel like Z-bar, PVC, curtain walls and steel decks

EXECUTION

EXAMINATION

    - Do not begin installation until substrates have been properly prepared.

If substrate preparation is the responsibility of another installer, notify General

Contractor, Architect, or other point of contact of unsatisfactory preparation before

proceeding.

Commencement of work outlined in this section shall be deemed as acceptance of

existing work and conditions.

PREPARATION

    - Clean surfaces thoroughly prior to installation.

Apply only when surfaces and environmental conditions are within limits prescribed

by the material manufacturer.

Prepare surfaces using the methods recommended by the manufacturer for

achieving the best result for the substrate under the project conditions.

It is recommended to install primer on oily surfaces and galvanized steel

INSTALLATION

    - Install in accordance with manufacturer's instructions.

Apply as recommended by manufacturer to thickness as indicated on drawings.

Equipment used to apply the foam insulation shall have fixed ratio positive

displacement pumps approved by foam manufacturer.

PROTECTION

    - Protect installed products until completion of project.

Touch-up, repair or replace damaged products before Substantial Completion.

# END OF SECTION 07 21 19